## Cabling Specifications
Cabling Specifications
Identifier | From | To | Signal |  | Cable | [5 empty] | Hazard Class | Comments | Ext comments
[5 empty] | Conductors |  |  | Insulation |  | Shielding
|  |  | Type | Voltage | Qty | Type | Material | Type | Min Voltage
| Main DAS Panel | Control Room | Ethernet | - | 2 | CAT-5 | - | - | - | No
|  | Test Section DAS Panel | Ehernet | - | 2 | CAT-5 | - | - | - | No
|  | SCR Panel | 4-20 mA Control | 24 | 11 | 2C-#14 | Cu | THHN | 600 | Yes |  | Twisted-shielded pair
|  |  | DIO | 24 | 11 | 2C-#14 | Cu | THHN | 600 | Yes |  | Twisted-shielded pair
|  |  | Power Transmitter | 24 | 11 | 2C-#14 | Cu | THHN | 600 | Yes |  | Twisted-shielded pair
|  | Thermocouples | Thermocouple | - | 40 | Type K TC Ext |  | - | - | Yes | Class 1 DIV 2 | Overall shielded
|  | Pressure Instruments | 4-20 mA Signal | 24 | 13 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Level Switches | DIO | 24 | 2 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Coriolis Flow Transmiter | 4-20 mA Signal | 24 | 2 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  |  | PWR | 120 | 2 | 3C-#14 | Cu | THHN | 600 | No | Class 1 DIV 2 |  | Separate conduit from signal wires
|  | EMFM |  |  | 1 |  |  |  |  | Yes | Class 1 DIV 2
|  | Valve Positioner | 4-20 mA Control | 24 | 5 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Valve Positioner feedback | 4-20 mA Signal | 24 | 5 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Valve Position Switch | DIO | 24 | 26 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair | 2 per Primary Loop on/off valve
|  | Solenoid Valve | DIO | 24 | 25 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Damper Actuator | 4-20 mA Control | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2
|  |  | PWR | 120 | 1 | 3C-#14 | Cu | THHN | 600 | No | Class 1 DIV 2
|  | VFD Panel | 4-20 mA Control | 24 | 6 | 2C-#14 | Cu | THHN | 300 | Yes |  | Twisted-shielded pair
|  |  | Speed feedback | 24 | 6 | 2C-#14 | Cu | THHN | 300 | Yes |  | Twisted-shielded pair
|  | T-001 Tray | Thermocouples | - | 4 | Type K TC Ext |  | - | - | Yes |  | Overall shielded
|  |  | Pressure Instruments | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes |  | Twisted-shielded pair
|  |  | Level Instruments | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes |  | Twisted, individual shielded pair
|  |  | Valve Limit Switches | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No |  | Twisted pair
|  | T-200 Tray | Thermocouples | - | 4 | Type K TC Ext |  | - | - | Yes |  | Overall shielded
|  |  | Pressure Instruments | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes |  | Twisted-shielded pair
|  |  | Level Instruments | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes |  | Twisted, individual shielded pair
|  |  | Valve Limit Switches | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No |  | Twisted pair
|  | T-900 Tray | Thermocouples | - | 4 | Type K TC Ext |  | - | - | Yes |  | Overall shielded
|  |  | Pressure Instruments | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes |  | Twisted-shielded pair
|  |  | Level Instruments | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes |  | Twisted, individual shielded pair | 2 per Primary Loop on/off valve
|  |  | Valve Limit Switches | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No |  | Twisted pair
| T-200 Tray | Thermocouples | Thermocouple | - | 4 | Type K TC Ext |  |  |  | Yes | Class 1 DIV 2 | Overall shielded
|  | Pressure Instruments | 4-20 mA Signal | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Level Instruments | 4-20 mA/Frequency | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted, individual shielded pair
|  | Valve Limit Switches | DIO | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No | Class 1 DIV 2 | Twisted pair | 2 per Primary Loop on/off valve
| T-900 Tray | Thermocouples | Thermocouple | - | 4 | Type K TC Ext |  |  |  | Yes | Class 1 DIV 2 | Overall shielded
|  | Pressure Instruments | 4-20 mA Signal | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Level Instruments | 4-20 mA/Frequency | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted, individual shielded pair
|  | Valve Limit Switches | DIO | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No | Class 1 DIV 2 | Twisted pair
| T-001 Tray | Thermocouples | Thermocouple | - | 4 | Type K TC Ext |  |  |  | Yes | Class 1 DIV 2 | Overall shielded
|  | Pressure Instruments | 4-20 mA Signal | 24 | 1 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Level Instruments | 4-20 mA/Frequency | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted, individual shielded pair
|  | Valve Limit Switches | DIO | 24 | 6 | 2C-#14 | Cu | THHN | 300 | No | Class 1 DIV 2 | Twisted pair | 2 per Primary Loop on/off valve
| Test Section DAS Panel | Thermocouples | Thermocouple | - | 34 | Type K TC Ext |  | - | - | Yes | Class 1 DIV 2 | Overall shielded
|  | Pressure Instruments | 4-20 mA Signal | 24 | 7 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
|  | Level Sensor | 4-20 mA/Frequency | 24 | 1 | 4C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted, individual shielded pair
|  | Level Switches | DIO | 24 | 4 | 2C-#14 | Cu | THHN | 300 | Yes | Class 1 DIV 2 | Twisted-shielded pair
| AC-2 (CMI) | Control Room | Ethernet | - | 2 | CAT-5 | - | - | - | No